**Clarifications**

|  |  |
| --- | --- |
| Tender: | ERDF.05.0121 – Tender 019  Tender for Mechanical and Electrical Engineering as part of ERDF Project ERDF.05.121 – Wildlife Rehabilitation Centre |
|  |  |
| No | Clarification |
| Q 1 | **Query**  Kindly requesting to provide clarifications for the below mentioned comments  • With reference to the UPS in BOQ it's mentioned that UPS of 10kva but the Specs say 2kva, Kindly confirm which one to consider  • If 10 kva is it 3 phase in single out or 3 phase in 3 phase out |
| **Answer**  The UPS shall have a rating of 2kVA as indicated in the specifications. |
| Q2 | **Query**  The thermal accumulator is required as a horizontal type - can a vertical tank be used?​ |
| **Answer**  The thermal accumulator shall be of the horizontal type as per specifications, due to the height constraints beneath the viewing platform, where it shall be installed. |
| Q3 | **Query**  The solar collectors are vacuum tube type - can flat plate type be used?​ - |
| **Answer**  The solar collectors shall be of the vacuum tube type as per specifications. |
| Q4 | **Query**  Can you confirm that 4 square metres of solar collectors are required for a thermal accumulator of 2000 litres? |
| **Answer**  The tenderers are to quote for a 4m2 solar collector as indicated in the specifications, having quantity as indicated in the BOQ. |
|  | No More Queries so far |
|  |

|  |  |  |
| --- | --- | --- |
| Deadline for request for any additional information from the NGO  **Clarification requests should be addressed to: *info@naturetrustmalta.org*** | Sunday 18th October 2020 | 12:00 hrs  (noon) |
| Last date on which additional information can be issued by the NGO | Friday 23rd October 2020 | 12:00 hrs  (noon) |

Date of Document – 14 October 2020