**Clarifications**

|  |  |
| --- | --- |
| Tender: | ERDF.05.0121 – Tender 019Tender for Mechanical and Electrical Engineering as part of ERDF Project ERDF.05.121 – Wildlife Rehabilitation Centre  |
|  |  |
| No | Clarification |
| Q 1 | **Query**Kindly requesting to provide clarifications for the below mentioned comments• With reference to the UPS in BOQ it's mentioned that UPS of 10kva but the Specs say 2kva, Kindly confirm which one to consider • If 10 kva is it 3 phase in single out or 3 phase in 3 phase out |
| **Answer**The UPS shall have a rating of 2kVA as indicated in the specifications. |
| Q2 | **Query**The thermal accumulator is required as a horizontal type - can a vertical tank be used?​ |
| **Answer**The thermal accumulator shall be of the horizontal type as per specifications, due to the height constraints beneath the viewing platform, where it shall be installed. |
| Q3 | **Query**The solar collectors are vacuum tube type - can flat plate type be used?​ - |
| **Answer**The solar collectors shall be of the vacuum tube type as per specifications. |
| Q4 | **Query**Can you confirm that 4 square metres of solar collectors are required for a thermal accumulator of 2000 litres?  |
| **Answer**The tenderers are to quote for a 4m2 solar collector as indicated in the specifications, having quantity as indicated in the BOQ. |
|  | No More Queries so far |
|  |

|  |  |  |
| --- | --- | --- |
| Deadline for request for any additional information from the NGO**Clarification requests should be addressed to: *info@naturetrustmalta.org*** | Sunday 18th October 2020 | 12:00 hrs(noon) |
| Last date on which additional information can be issued by the NGO | Friday 23rd October 2020 | 12:00 hrs(noon) |

Date of Document – 14 October 2020